## Anel
Variável | Descrição | Sec | Sub | Dis | Dev | Idx | Prop | EPICS | RS Logix | Tipo de dado | Input/Output | EGU | TAG
1 | Detector de Arco Sistema A | RA | TL | RF | ArcDetec | SIA | Sts-Mon | RA-TL:RF-ArcDetec-SIA:Sts-Mon
2 | Detector de Arco Sistema A Analogico | RA | TL | RF | ArcDetec | SIA | Analog-Mon | RA-TL:RF-ArcDetec-SIA:Analog-Mon
3 | Sistema de Interlock circulador operacional | RA | TL | RF | Circulator | SIA | IntlkOp-Mon | RA-TL:RF-Circulator-SIA:IntlkOp-Mon
4 | Aquecedor do Circulador | RA | TL | RF | Circulator | SIA | HeaterSts-Mon | RA-TL:RF-Circulator-SIA:HeaterSts-Mon
5 | Interlock Circulador Operacional | RA | TL | RF | Circulator | SIA | IntlkOpSts-Mon | RA-TL:RF-Circulator-SIA:IntlkOpSts-Mon
6 | Vazão do Circulador | RA | TL | RF | Circulator | SIA | FlwRt-Mon | RA-TL:RF-Circulator-SIA:FlwRt-Mon
7 | Bobinas do Circulador | RA | TL | RF | Circulator | SIA | Sts-Mon | RA-TL:RF-Circulator-SIA:Sts-Mon
8 | Temp. do Circulador Abaixo do Set | RA | TL | RF | Circulator | SIA | TDown-Mon | RA-TL:RF-Circulator-SIA:TDown-Mon
9 | Temp. do Circulador Acima do Set | RA | TL | RF | Circulator | SIA | TUp-Mon | RA-TL:RF-Circulator-SIA:TUp-Mon
10 | Drift de Temp. do Circulador Alto | RA | TL | RF | Circulator | SIA | TDrift-Mon | RA-TL:RF-Circulator-SIA:TDrift-Mon
11 | Temp. Ambiente Abaixo do Set | RA | TL | RF | Circulator | SIA | TEnvi-Mon | RA-TL:RF-Circulator-SIA:TEnvi-Mon
12 | Vazão Carga 300kW | RA | TL | RF | Circulator | SIA | LoadFlwRt-Mon | RA-TL:RF-Circulator-SIA:LoadFlwRt-Mon
13 | Interlock geral Circulador | RA | TL | RF | Circulator | SIA | Sts-Mon | RA-TL:RF-Circulator-SIA:Sts-Mon
14 | Torre 01 do Anel Termostato da Barra Dissipadora 01A | RA | ToSIA01 | RF | HeatSink | H01A | Tms-Mon | RA-ToSIA01:RF-HeatSink-H01A:Tms-Mon
15 | Torre 01 do Anel Termostato da Barra Dissipadora 01B | RA | ToSIA01 | RF | HeatSink | H01B | Tms-Mon | RA-ToSIA01:RF-HeatSink-H01B:Tms-Mon
16 | Torre 01 do Anel Termostato da Barra Dissipadora 02A | RA | ToSIA01 | RF | HeatSink | H02A | Tms-Mon | RA-ToSIA01:RF-HeatSink-H02A:Tms-Mon
17 | Torre 01 do Anel Termostato da Barra Dissipadora 02B | RA | ToSIA01 | RF | HeatSink | H02B | Tms-Mon | RA-ToSIA01:RF-HeatSink-H02B:Tms-Mon
18 | Torre 01 do Anel Termostato da Barra Dissipadora 03A | RA | ToSIA01 | RF | HeatSink | H03A | Tms-Mon | RA-ToSIA01:RF-HeatSink-H03A:Tms-Mon
19 | Torre 01 do Anel Termostato da Barra Dissipadora 03B | RA | ToSIA01 | RF | HeatSink | H03B | Tms-Mon | RA-ToSIA01:RF-HeatSink-H03B:Tms-Mon
20 | Torre 01 do Anel Termostato da Barra Dissipadora 04A | RA | ToSIA01 | RF | HeatSink | H04A | Tms-Mon | RA-ToSIA01:RF-HeatSink-H04A:Tms-Mon
21 | Torre 01 do Anel Termostato da Barra Dissipadora 04B | RA | ToSIA01 | RF | HeatSink | H04B | Tms-Mon | RA-ToSIA01:RF-HeatSink-H04B:Tms-Mon
22 | Torre 01 do Anel Termostato da Barra Dissipadora 05A | RA | ToSIA01 | RF | HeatSink | H05A | Tms-Mon | RA-ToSIA01:RF-HeatSink-H05A:Tms-Mon
23 | Torre 01 do Anel Termostato da Barra Dissipadora 05B | RA | ToSIA01 | RF | HeatSink | H05B | Tms-Mon | RA-ToSIA01:RF-HeatSink-H05B:Tms-Mon
24 | Torre 01 do Anel Termostato da Barra Dissipadora 06A | RA | ToSIA01 | RF | HeatSink | H06A | Tms-Mon | RA-ToSIA01:RF-HeatSink-H06A:Tms-Mon
25 | Torre 01 do Anel Termostato da Barra Dissipadora 06B | RA | ToSIA01 | RF | HeatSink | H06B | Tms-Mon | RA-ToSIA01:RF-HeatSink-H06B:Tms-Mon
26 | Torre 01 do Anel Termostato da Barra Dissipadora 07A | RA | ToSIA01 | RF | HeatSink | H07A | Tms-Mon | RA-ToSIA01:RF-HeatSink-H07A:Tms-Mon
27 | Torre 01 do Anel Termostato da Barra Dissipadora 07B | RA | ToSIA01 | RF | HeatSink | H07B | Tms-Mon | RA-ToSIA01:RF-HeatSink-H07B:Tms-Mon
28 | Torre 01 do Anel Termostato da Barra Dissipadora 08A | RA | ToSIA01 | RF | HeatSink | H08A | Tms-Mon | RA-ToSIA01:RF-HeatSink-H08A:Tms-Mon
29 | Torre 01 do Anel Termostato da Barra Dissipadora 08B | RA | ToSIA01 | RF | HeatSink | H08B | Tms-Mon | RA-ToSIA01:RF-HeatSink-H08B:Tms-Mon
30 | PT- 100 Torre 01 Barra Dissipadora 01A | RA | ToSIA01 | RF | HeatSink | H01A | T-Mon | RA-ToSIA01:RF-HeatSink-H01A:T-Mon
31 | PT- 100 Torre 01 Barra Dissipadora 01B | RA | ToSIA01 | RF | HeatSink | H01B | T-Mon | RA-ToSIA01:RF-HeatSink-H01B:T-Mon
32 | PT- 100 Torre 01 Barra Dissipadora 02A | RA | ToSIA01 | RF | HeatSink | H02A | T-Mon | RA-ToSIA01:RF-HeatSink-H02A:T-Mon
33 | PT- 100 Torre 01 Barra Dissipadora 02B | RA | ToSIA01 | RF | HeatSink | H02B | T-Mon | RA-ToSIA01:RF-HeatSink-H02B:T-Mon
34 | PT- 100 Torre 01 Barra Dissipadora 03A | RA | ToSIA01 | RF | HeatSink | H03A | T-Mon | RA-ToSIA01:RF-HeatSink-H03A:T-Mon
35 | PT- 100 Torre 01 Barra Dissipadora 03B | RA | ToSIA01 | RF | HeatSink | H03B | T-Mon | RA-ToSIA01:RF-HeatSink-H03B:T-Mon
36 | PT- 100 Torre 01 Barra Dissipadora 04A | RA | ToSIA01 | RF | HeatSink | H04A | T-Mon | RA-ToSIA01:RF-HeatSink-H04A:T-Mon
37 | PT- 100 Torre 01 Barra Dissipadora 04B | RA | ToSIA01 | RF | HeatSink | H04B | T-Mon | RA-ToSIA01:RF-HeatSink-H04B:T-Mon
38 | PT- 100 Torre 01 Barra Dissipadora 05A | RA | ToSIA01 | RF | HeatSink | H05A | T-Mon | RA-ToSIA01:RF-HeatSink-H05A:T-Mon
39 | PT- 100 Torre 01 Barra Dissipadora 05B | RA | ToSIA01 | RF | HeatSink | H05B | T-Mon | RA-ToSIA01:RF-HeatSink-H05B:T-Mon
40 | PT- 100 Torre 01 Barra Dissipadora 06A | RA | ToSIA01 | RF | HeatSink | H06A | T-Mon | RA-ToSIA01:RF-HeatSink-H06A:T-Mon
41 | PT- 100 Torre 01 Barra Dissipadora 06B | RA | ToSIA01 | RF | HeatSink | H06B | T-Mon | RA-ToSIA01:RF-HeatSink-H06B:T-Mon
42 | PT- 100 Torre 01 Barra Dissipadora 07A | RA | ToSIA01 | RF | HeatSink | H07A | T-Mon | RA-ToSIA01:RF-HeatSink-H07A:T-Mon
43 | PT- 100 Torre 01 Barra Dissipadora 07B | RA | ToSIA01 | RF | HeatSink | H07B | T-Mon | RA-ToSIA01:RF-HeatSink-H07B:T-Mon
44 | PT- 100 Torre 01 Barra Dissipadora 08A | RA | ToSIA01 | RF | HeatSink | H08A | T-Mon | RA-ToSIA01:RF-HeatSink-H08A:T-Mon
45 | PT- 100 Torre 01 Barra Dissipadora 08B | RA | ToSIA01 | RF | HeatSink | H08B | T-Mon | RA-ToSIA01:RF-HeatSink-H08B:T-Mon
46 | Torre 02 do Anel Termostato da Barra Dissipadora 01A | RA | ToSIA02 | RF | HeatSink | H01A | Tms-Mon | RA-ToSIA02:RF-HeatSink-H01A:Tms-Mon
47 | Torre 02 do Anel Termostato da Barra Dissipadora 01B | RA | ToSIA02 | RF | HeatSink | H01B | Tms-Mon | RA-ToSIA02:RF-HeatSink-H01B:Tms-Mon
48 | Torre 02 do Anel Termostato da Barra Dissipadora 02A | RA | ToSIA02 | RF | HeatSink | H02A | Tms-Mon | RA-ToSIA02:RF-HeatSink-H02A:Tms-Mon
49 | Torre 02 do Anel Termostato da Barra Dissipadora 02B | RA | ToSIA02 | RF | HeatSink | H02B | Tms-Mon | RA-ToSIA02:RF-HeatSink-H02B:Tms-Mon
50 | Torre 02 do Anel Termostato da Barra Dissipadora 03A | RA | ToSIA02 | RF | HeatSink | H03A | Tms-Mon | RA-ToSIA02:RF-HeatSink-H03A:Tms-Mon
51 | Torre 02 do Anel Termostato da Barra Dissipadora 03B | RA | ToSIA02 | RF | HeatSink | H03B | Tms-Mon | RA-ToSIA02:RF-HeatSink-H03B:Tms-Mon
52 | Torre 02 do Anel Termostato da Barra Dissipadora 04A | RA | ToSIA02 | RF | HeatSink | H04A | Tms-Mon | RA-ToSIA02:RF-HeatSink-H04A:Tms-Mon
53 | Torre 02 do Anel Termostato da Barra Dissipadora 04B | RA | ToSIA02 | RF | HeatSink | H04B | Tms-Mon | RA-ToSIA02:RF-HeatSink-H04B:Tms-Mon
54 | Torre 02 do Anel Termostato da Barra Dissipadora 05A | RA | ToSIA02 | RF | HeatSink | H05A | Tms-Mon | RA-ToSIA02:RF-HeatSink-H05A:Tms-Mon
55 | Torre 02 do Anel Termostato da Barra Dissipadora 05B | RA | ToSIA02 | RF | HeatSink | H05B | Tms-Mon | RA-ToSIA02:RF-HeatSink-H05B:Tms-Mon
56 | Torre 02 do Anel Termostato da Barra Dissipadora 06A | RA | ToSIA02 | RF | HeatSink | H06A | Tms-Mon | RA-ToSIA02:RF-HeatSink-H06A:Tms-Mon
57 | Torre 02 do Anel Termostato da Barra Dissipadora 06B | RA | ToSIA02 | RF | HeatSink | H06B | Tms-Mon | RA-ToSIA02:RF-HeatSink-H06B:Tms-Mon
58 | Torre 02 do Anel Termostato da Barra Dissipadora 07A | RA | ToSIA02 | RF | HeatSink | H07A | Tms-Mon | RA-ToSIA02:RF-HeatSink-H07A:Tms-Mon
59 | Torre 02 do Anel Termostato da Barra Dissipadora 07B | RA | ToSIA02 | RF | HeatSink | H07B | Tms-Mon | RA-ToSIA02:RF-HeatSink-H07B:Tms-Mon
60 | Torre 02 do Anel Termostato da Barra Dissipadora 08A | RA | ToSIA02 | RF | HeatSink | H08A | Tms-Mon | RA-ToSIA02:RF-HeatSink-H08A:Tms-Mon
61 | Torre 02 do Anel Termostato da Barra Dissipadora 08B | RA | ToSIA02 | RF | HeatSink | H08B | Tms-Mon | RA-ToSIA02:RF-HeatSink-H08B:Tms-Mon
62 | PT- 100 Torre 02 Barra Dissipadora 01A | RA | ToSIA02 | RF | HeatSink | H01A | T-Mon | RA-ToSIA02:RF-HeatSink-H01A:T-Mon
63 | PT- 100 Torre 02 Barra Dissipadora 01B | RA | ToSIA02 | RF | HeatSink | H01B | T-Mon | RA-ToSIA02:RF-HeatSink-H01B:T-Mon
64 | PT- 100 Torre 02 Barra Dissipadora 02A | RA | ToSIA02 | RF | HeatSink | H02A | T-Mon | RA-ToSIA02:RF-HeatSink-H02A:T-Mon
65 | PT- 100 Torre 02 Barra Dissipadora 02B | RA | ToSIA02 | RF | HeatSink | H02B | T-Mon | RA-ToSIA02:RF-HeatSink-H02B:T-Mon
66 | PT- 100 Torre 02 Barra Dissipadora 03A | RA | ToSIA02 | RF | HeatSink | H03A | T-Mon | RA-ToSIA02:RF-HeatSink-H03A:T-Mon
67 | PT- 100 Torre 02 Barra Dissipadora 03B | RA | ToSIA02 | RF | HeatSink | H03B | T-Mon | RA-ToSIA02:RF-HeatSink-H03B:T-Mon
68 | PT- 100 Torre 02 Barra Dissipadora 04A | RA | ToSIA02 | RF | HeatSink | H04A | T-Mon | RA-ToSIA02:RF-HeatSink-H04A:T-Mon
69 | PT- 100 Torre 02 Barra Dissipadora 04B | RA | ToSIA02 | RF | HeatSink | H04B | T-Mon | RA-ToSIA02:RF-HeatSink-H04B:T-Mon
70 | PT- 100 Torre 02 Barra Dissipadora 05A | RA | ToSIA02 | RF | HeatSink | H05A | T-Mon | RA-ToSIA02:RF-HeatSink-H05A:T-Mon
71 | PT- 100 Torre 02 Barra Dissipadora 05B | RA | ToSIA02 | RF | HeatSink | H05B | T-Mon | RA-ToSIA02:RF-HeatSink-H05B:T-Mon
72 | PT- 100 Torre 02 Barra Dissipadora 06A | RA | ToSIA02 | RF | HeatSink | H06A | T-Mon | RA-ToSIA02:RF-HeatSink-H06A:T-Mon
73 | PT- 100 Torre 02 Barra Dissipadora 06B | RA | ToSIA02 | RF | HeatSink | H06B | T-Mon | RA-ToSIA02:RF-HeatSink-H06B:T-Mon
74 | PT- 100 Torre 02 Barra Dissipadora 07A | RA | ToSIA02 | RF | HeatSink | H07A | T-Mon | RA-ToSIA02:RF-HeatSink-H07A:T-Mon
75 | PT- 100 Torre 02 Barra Dissipadora 07B | RA | ToSIA02 | RF | HeatSink | H07B | T-Mon | RA-ToSIA02:RF-HeatSink-H07B:T-Mon
76 | PT- 100 Torre 02 Barra Dissipadora 08A | RA | ToSIA02 | RF | HeatSink | H08A | T-Mon | RA-ToSIA02:RF-HeatSink-H08A:T-Mon
77 | PT- 100 Torre 02 Barra Dissipadora 08B | RA | ToSIA02 | RF | HeatSink | H08B | T-Mon | RA-ToSIA02:RF-HeatSink-H08B:T-Mon
78 | Sistema Anel A Interlock Sirius | SI | 03SP | RF | Intlk | - | SIA-Mon | SI-03SP:RF-Intlk:SIA-Mon
79 | Interlock LLRF | SI | 03SP | RF | Intlk | - | LLRF-Mon | SI-03SP:RF-Intlk:LLRF-Mon
80 | Botão de emergencia do sistema de interlock | SI | 03SP | RF | Intlk | - | EStop-Mon | SI-03SP:RF-Intlk:EStop-Mon
81 | Reset de Falhas (Reseta todas as falhas do sistema remotamente | SI | 03SP | RF | Intlk | - | Reset-Sel | SI-03SP:RF-Intlk:Reset-Sel
82 | LLRF Operacional | SI | 03SP | RF | LLRF | - | Status-Mon | SI-03SP:RF-LLRF:Status-Mon
83 | Interlock LLRF | SI | 03SP | RF | LLRF | - | Intlk-Mon | SI-03SP:RF-LLRF:Intlk-Mon
84 | Termostato Pré-Amplificador 01 | SI | 03SP | RF | LLRFPreAmp | 01 | Tms-Mon | SI-03SP:RF-LLRFPreAmp-01:Tms-Mon
85 | PT- 100 Torre 01 Pré-Amplificador | SI | 03SP | RF | LLRFPreAmp | 01 | T-Mon | SI-03SP:RF-LLRFPreAmp-01:T-Mon
86 | Termostato Pré-Amplificador 02 | SI | 03SP | RF | LLRFPreAmp | 02 | Tms-Mon | SI-03SP:RF-LLRFPreAmp-02:Tms-Mon
87 | PT- 100 Torre 02 Pré-Amplificador | SI | 03SP | RF | LLRFPreAmp | 02 | T-Mon | SI-03SP:RF-LLRFPreAmp-02:T-Mon
88 | Vácuo Petra VII | SI | 03SP | RF | P7Cav | - | Pressure -Mon | SI-03SP:RF-P7Cav:Pressure -Mon
89 | Chave de Fluxo 01 Petra VII | SI | 03SP | RF | P7Cav | - | HDFlwRt1-Mon | SI-03SP:RF-P7Cav:HDFlwRt1-Mon
90 | Chave de Fluxo 02 Petra VII | SI | 03SP | RF | P7Cav | - | HDFlwRt2-Mon | SI-03SP:RF-P7Cav:HDFlwRt2-Mon
91 | Chave de Fluxo 03 Petra VII | SI | 03SP | RF | P7Cav | - | HDFlwRt3-Mon | SI-03SP:RF-P7Cav:HDFlwRt3-Mon
92 | Sensor de Pressão Petra VII | SI | 03SP | RF | P7Cav | - | CoupPressure -Mon | SI-03SP:RF-P7Cav:CoupPressure -Mon
93 | PT - 100 01 PetraVII | SI | 03SP | RF | P7Cav | - | Disc1T-Mon | SI-03SP:RF-P7Cav:Disc1T-Mon
94 | PT - 100 02 PetraVII | SI | 03SP | RF | P7Cav | - | Disc2T-Mon | SI-03SP:RF-P7Cav:Disc2T-Mon
95 | PT - 100 03 PetraVII | SI | 03SP | RF | P7Cav | - | Disc3T-Mon | SI-03SP:RF-P7Cav:Disc3T-Mon
96 | PT - 100 04 PetraVII | SI | 03SP | RF | P7Cav | - | Disc4T-Mon | SI-03SP:RF-P7Cav:Disc4T-Mon
97 | PT - 100 05 PetraVII | SI | 03SP | RF | P7Cav | - | Disc5T-Mon | SI-03SP:RF-P7Cav:Disc5T-Mon
98 | PT - 100 06 PetraVII | SI | 03SP | RF | P7Cav | - | Disc6T-Mon | SI-03SP:RF-P7Cav:Disc6T-Mon
99 | PT - 100 07 PetraVII | SI | 03SP | RF | P7Cav | - | Disc7T-Mon | SI-03SP:RF-P7Cav:Disc7T-Mon
100 | Acoplador Petra VII | SI | 03SP | RF | P7Cav | - | CoupT-Mon | SI-03SP:RF-P7Cav:CoupT-Mon
101 | Interlock Geral Petra 7 | SI | 03SP | RF | P7Cav | - | Sts-Mon | SI-03SP:RF-P7Cav:Sts-Mon
102 | Emergência Interlock Torre 1 | RA | ToSIA01 | RF | SSAmpTower | - | EStop-Mon | RA-ToSIA01:RF-SSAmpTower:EStop-Mon
103 | Emergência Interlock Torre2 | RA | ToSIA02 | RF | SSAmpTower | - | EStop-Mon | RA-ToSIA02:RF-SSAmpTower:EStop-Mon
104 | Potência total de RF Anel A | RA | ToSIA01 | RF | SSAmpTower | - | PwrRF-Mon | RA-ToSIA01:RF-SSAmpTower:PwrRF-Mon
105 | Chave Pin Lenta Torre 01 | RA | ToSIA01 | RF | SSAmpTower | - | PINSw-Mon | RA-ToSIA01:RF-SSAmpTower:PINSw-Mon
106 | Status do Painel AC da Torre 01 do Anel | RA | ToSIA01 | RF | SSAmpTower | - | PwrACOp-Mon | RA-ToSIA01:RF-SSAmpTower:PwrACOp-Mon
107 | Falta de Fase do Painel Torre 01 do Anel | RA | ToSIA01 | RF | SSAmpTower | - | PhsFlt-Mon | RA-ToSIA01:RF-SSAmpTower:PhsFlt-Mon
108 | Rotâmetro Torre 01 do Anel | RA | ToSIA01 | RF | SSAmpTower | - | HDFlwRt-Mon | RA-ToSIA01:RF-SSAmpTower:HDFlwRt-Mon
109 | Desabilita AC das Fontes TDK Torre 01 | RA | ToSIA01 | RF | SSAmpTower | - | PwrACDsbl-Sel | RA-ToSIA01:RF-SSAmpTower:PwrACDsbl-Sel
110 | Habilita AC das Fontes TDK Torre 01 | RA | ToSIA01 | RF | SSAmpTower | - | PwrACEnbl-Sel | RA-ToSIA01:RF-SSAmpTower:PwrACEnbl-Sel
111 | Lê estado de potência AC das Fontes TDK Torre 01 | RA | ToSIA01 | RF | SSAmpTower | - | PwrACS-Sts | RA-ToSIA01:RF-SSAmpTower:PwrACS-Sts
112 | Desabilita Saída de 48V das Fontes TDK Torre 01 | RA | ToSIA01 | RF | SSAmpTower | - | PwrDCDsbl-Sel | RA-ToSIA01:RF-SSAmpTower:PwrDCDsbl-Sel
113 | Libera Saída de 48V das Fontes TDK Torre 01 | RA | ToSIA01 | RF | SSAmpTower | - | PwrDCEnbl-Sel | RA-ToSIA01:RF-SSAmpTower:PwrDCEnbl-Sel
114 | Lê saída 48V das Fontes TDK Torre 01 | RA | ToSIA01 | RF | SSAmpTower | - | PwrDC-Sts | RA-ToSIA01:RF-SSAmpTower:PwrDC-Sts
115 | Interlock externo do Painel Torre 01 | RA | ToSIA01 | RF | SSAmpTower | - | Intlk-Mon | RA-ToSIA01:RF-SSAmpTower:Intlk-Mon
116 | Chave Pin Lenta Torre 02 | RA | ToSIA02 | RF | SSAmpTower | - | PINSw-Mon | RA-ToSIA02:RF-SSAmpTower:PINSw-Mon
117 | Status do Painel AC da Torre 02 do Anel | RA | ToSIA02 | RF | SSAmpTower | - | PwrACOp-Mon | RA-ToSIA02:RF-SSAmpTower:PwrACOp-Mon
116 | Falta de Fase do Painel Torre 02 do Anel | RA | ToSIA02 | RF | SSAmpTower | - | PhsFlt-Mon | RA-ToSIA02:RF-SSAmpTower:PhsFlt-Mon
117 | Rotâmetro Torre 02 do Anel | RA | ToSIA02 | RF | SSAmpTower | - | HdFlwRt-Mon | RA-ToSIA02:RF-SSAmpTower:HdFlwRt-Mon
118 | Desabilita AC das Fontes TDK Torre 02 | RA | ToSIA02 | RF | SSAmpTower | - | PwrACDsbl-Sel | RA-ToSIA02:RF-SSAmpTower:PwrACDsbl-Sel
119 | Habilita AC das Fontes TDK Torre 02 | RA | ToSIA02 | RF | SSAmpTower | - | PwrACEnbl-Sel | RA-ToSIA02:RF-SSAmpTower:PwrACEnbl-Sel
120 | Lê AC das Fontes TDK Torre 02 | RA | ToSIA02 | RF | SSAmpTower | - | PwrAC-Sts | RA-ToSIA02:RF-SSAmpTower:PwrAC-Sts
121 | Desabilita Saída de 48V das Fontes TDK Torre 02 | RA | ToSIA02 | RF | SSAmpTower | - | PwrDCDsbl-Sel | RA-ToSIA02:RF-SSAmpTower:PwrDCDsbl-Sel
122 | Libera Saída de 48V das Fontes TDK Torre 02 | RA | ToSIA02 | RF | SSAmpTower | - | PwrDCEnbl-Sel | RA-ToSIA02:RF-SSAmpTower:PwrDCEnbl-Sel
123 | Lê Saída de 48V das Fontes TDK Torre 02 | RA | ToSIA02 | RF | SSAmpTower | - | PwrDC-Sts | RA-ToSIA02:RF-SSAmpTower:PwrDC-Sts
124 | Interlock externo do Painel Torre 02 | RA | ToSIA02 | RF | SSAmpTower | - | Intlk-Mon | RA-ToSIA02:RF-SSAmpTower:Intlk-Mon
125 | Interlock Geral SSA 1 | RA | ToSIA01 | RF | SSAmpTower | - | Sts-Mon | RA-ToSIA01:RF-SSAmpTower:Sts-Mon
126 | Interlock Geral SSA 2 | RA | ToSIA02 | RF | SSAmpTower | - | Sts-Mon | RA-ToSIA02:RF-SSAmpTower:Sts-Mon
127 | Falha Ac Mini Rack 1 Torre 1 | RA | ToSIA01 | RF | TDKSource | R1 | StsAC-Mon | RA-ToSIA01:RF-TDKSource-R1:StsAC-Mon
128 | Falha Ac Mini Rack 2 Torre 1 | RA | ToSIA01 | RF | TDKSource | R2 | StsAC-Mon | RA-ToSIA01:RF-TDKSource-R2:StsAC-Mon
129 | Falha Ac Mini Rack 3 Torre 1 | RA | ToSIA01 | RF | TDKSource | R3 | StsAC-Mon | RA-ToSIA01:RF-TDKSource-R3:StsAC-Mon
130 | Falha Ac Mini Rack 4 Torre 1 | RA | ToSIA01 | RF | TDKSource | R4 | StsAC-Mon | RA-ToSIA01:RF-TDKSource-R4:StsAC-Mon
131 | Falha Ac Mini Rack 1 Torre 2 | RA | ToSIA02 | RF | TDKSource | R1 | StsAC-Mon | RA-ToSIA02:RF-TDKSource-R1:StsAC-Mon
132 | Falha Ac Mini Rack 2 Torre 2 | RA | ToSIA02 | RF | TDKSource | R2 | StsAC-Mon | RA-ToSIA02:RF-TDKSource-R2:StsAC-Mon
133 | Falha Ac Mini Rack 3 Torre 2 | RA | ToSIA02 | RF | TDKSource | R3 | StsAC-Mon | RA-ToSIA02:RF-TDKSource-R3:StsAC-Mon
134 | Falha Ac Mini Rack 4 Torre 2 | RA | ToSIA02 | RF | TDKSource | R4 | StsAC-Mon | RA-ToSIA02:RF-TDKSource-R4:StsAC-Mon
135 | Interlock geral Linha de Transmissao | RA | TL | RF | TrLine | SIA | Sts-Mon | RA-TL:RF-TrLine-SIA:Sts-Mon
Note on A13: Ranieri Ramires do Canto Santos: Da Variável 13 a 16 ainda não esta definido.
Note on B14: Necessário explicação da aplicação.

## Devices
Super Section | Section | Subsection | Discipline | Device Type | Instance Index | Description
| RA | TL | RF | ArcDetec | BO |  | RATLRFArcDetecBO
| RA | TL | RF | Circulator | BO |  | RATLRFCirculatorBO
| RA | ToBO | RF | HeatSink | H01 |  | RAToBORFHeatSinkH01
| RA | ToBO | RF | HeatSink | H02 |  | RAToBORFHeatSinkH02
| RA | ToBO | RF | HeatSink | H03 |  | RAToBORFHeatSinkH03
| RA | ToBO | RF | HeatSink | H04 |  | RAToBORFHeatSinkH04
| RA | ToBO | RF | HeatSink | H05 |  | RAToBORFHeatSinkH05
| RA | ToBO | RF | HeatSink | H06 |  | RAToBORFHeatSinkH06
| BO | 05D | RF | Intlk | - |  | BO05DRFIntlk-
| BO | 05D | RF | LLRF | - |  | BO05DRFLLRF-
| BO | 05D | RF | LLRFPreAmp | - |  | BO05DRFLLRFPreAmp-
| BO | 05D | RF | P5Cav | - |  | BO05DRFP5Cav-
| RA | ToBO | RF | SSAmpTower | - |  | RAToBORFSSAmpTower-
| BO | ToBO | RF | SSAmpTower | - |  | BOToBORFSSAmpTower-
| RA | TL | RF | TrLine | BO |  | RATLRFTrLineBO
| RA | TL | RF | Circulator | SIA |  | RATLRFCirculatorSIA
| RA | ToSIA01 | RF | HeatSink | H01A |  | RAToSIA01RFHeatSinkH01A
| RA | ToSIA01 | RF | HeatSink | H01B |  | RAToSIA01RFHeatSinkH01B
| RA | ToSIA01 | RF | HeatSink | H02A |  | RAToSIA01RFHeatSinkH02A
| RA | ToSIA01 | RF | HeatSink | H02B |  | RAToSIA01RFHeatSinkH02B
| RA | ToSIA01 | RF | HeatSink | H03A |  | RAToSIA01RFHeatSinkH03A
| RA | ToSIA01 | RF | HeatSink | H03B |  | RAToSIA01RFHeatSinkH03B
| RA | ToSIA01 | RF | HeatSink | H04A |  | RAToSIA01RFHeatSinkH04A
| RA | ToSIA01 | RF | HeatSink | H04B |  | RAToSIA01RFHeatSinkH04B
| RA | ToSIA01 | RF | HeatSink | H05A |  | RAToSIA01RFHeatSinkH05A
| RA | ToSIA01 | RF | HeatSink | H05B |  | RAToSIA01RFHeatSinkH05B
| RA | ToSIA01 | RF | HeatSink | H06A |  | RAToSIA01RFHeatSinkH06A
| RA | ToSIA01 | RF | HeatSink | H06B |  | RAToSIA01RFHeatSinkH06B
| RA | ToSIA01 | RF | HeatSink | H07A |  | RAToSIA01RFHeatSinkH07A
| RA | ToSIA01 | RF | HeatSink | H07B |  | RAToSIA01RFHeatSinkH07B
| RA | ToSIA01 | RF | HeatSink | H08A |  | RAToSIA01RFHeatSinkH08A
| RA | ToSIA01 | RF | HeatSink | H08B |  | RAToSIA01RFHeatSinkH08B
| RA | ToSIA02 | RF | HeatSink | H01A |  | RAToSIA02RFHeatSinkH01A
| RA | ToSIA02 | RF | HeatSink | H01B |  | RAToSIA02RFHeatSinkH01B
| RA | ToSIA02 | RF | HeatSink | H02A |  | RAToSIA02RFHeatSinkH02A
| RA | ToSIA02 | RF | HeatSink | H02B |  | RAToSIA02RFHeatSinkH02B
| RA | ToSIA02 | RF | HeatSink | H03A |  | RAToSIA02RFHeatSinkH03A
| RA | ToSIA02 | RF | HeatSink | H03B |  | RAToSIA02RFHeatSinkH03B
| RA | ToSIA02 | RF | HeatSink | H04A |  | RAToSIA02RFHeatSinkH04A
| RA | ToSIA02 | RF | HeatSink | H04B |  | RAToSIA02RFHeatSinkH04B
| RA | ToSIA02 | RF | HeatSink | H05A |  | RAToSIA02RFHeatSinkH05A
| RA | ToSIA02 | RF | HeatSink | H05B |  | RAToSIA02RFHeatSinkH05B
| RA | ToSIA02 | RF | HeatSink | H06A |  | RAToSIA02RFHeatSinkH06A
| RA | ToSIA02 | RF | HeatSink | H06B |  | RAToSIA02RFHeatSinkH06B
| RA | ToSIA02 | RF | HeatSink | H07A |  | RAToSIA02RFHeatSinkH07A
| RA | ToSIA02 | RF | HeatSink | H07B |  | RAToSIA02RFHeatSinkH07B
| RA | ToSIA02 | RF | HeatSink | H08A |  | RAToSIA02RFHeatSinkH08A
| RA | ToSIA02 | RF | HeatSink | H08B |  | RAToSIA02RFHeatSinkH08B
| SI | 03SP | RF | Intlk | - |  | SI03SPRFIntlk-
| SI | 03SP | RF | LLRF | - |  | SI03SPRFLLRF-
| SI | 03SP | RF | LLRFPreAmp | 02 |  | SI03SPRFLLRFPreAmp02
| SI | 03SP | RF | P7Cav | - |  | SI03SPRFP7Cav-
| RA | ToSIA01 | RF | SSAmpTower | - |  | RAToSIA01RFSSAmpTower-
| RA | ToSIA01 | RF | SSAmpTower | - |  | RAToSIA01RFSSAmpTower-
| RA | ToSIA02 | RF | SSAmpTower | - |  | RAToSIA02RFSSAmpTower-
| RA | ToSIA01 | RF | TDKSource | R1 |  | RAToSIA01RFTDKSourceR1
| RA | ToSIA01 | RF | TDKSource | R2 |  | RAToSIA01RFTDKSourceR2
| RA | ToSIA01 | RF | TDKSource | R3 |  | RAToSIA01RFTDKSourceR3
| RA | ToSIA01 | RF | TDKSource | R4 |  | RAToSIA01RFTDKSourceR4
| RA | ToSIA02 | RF | TDKSource | R1 |  | RAToSIA02RFTDKSourceR1
| RA | ToSIA02 | RF | TDKSource | R2 |  | RAToSIA02RFTDKSourceR2
| RA | ToSIA02 | RF | TDKSource | R3 |  | RAToSIA02RFTDKSourceR3
| RA | ToSIA02 | RF | TDKSource | R4 |  | RAToSIA02RFTDKSourceR4
| RA | TL | RF | ArcDetec | SIA |  | RATLRFArcDetecSIA

## Booster
Variável | Descrição | Sec | Sub | Dis | Dev | Idx | Prop | EPICS | RS Logix | Tipo de dado | Input/Output | EGU | TAG
1 | Detector de Arco | RA | TL | RF | ArcDetec | BO | Sts-Mon | RA-TL:RF-ArcDetec-BO:Sts-Mon | Memorias[1].5 | Digital | Input |  | Memorias[1] B 5
2 | Detector de Arco Sistema A Analogico | RA | TL | RF | ArcDetec | BO | Analog-Mon | RA-TL:RF-ArcDetec-BO:Analog-Mon | N/A | N/A | N/A |  | N/A
3 | Aquecedor - via Controlador do Circulador | RA | TL | RF | Circulator | BO | Heater-Mon | RA-TL:RF-Circulator-BO:Heater-Mon | Memorias[0].28 | Digital | Input |  | Memorias[0] B 28
4 | Sistema de Interlock circulador operacional | RA | TL | RF | Circulator | BO | IntlkOp-Mon | RA-TL:RF-Circulator-BO:IntlkOp-Mon | Memorias[0].29 | Digital | Input |  | Memorias[0] B 29
5 | Vazão Circulador - Via Skid | RA | TL | RF | Circulator | BO | FlwRt-Mon | RA-TL:RF-Circulator-BO:FlwRt-Mon | Memorias[0].30 | Digital | Input |  | Memorias[0] B 30
6 | Bobinas do circulador | RA | TL | RF | Circulator | BO | Sts-Mon | EPICS | Memorias[1].0 | Digital | Input |  | Memorias[1] B 0
7 | Temp. do Circulador Abaixo do Set | RA | TL | RF | Circulator | BO | TDown-Mon | RA-TL:RF-Circulator-BO:TDown-Mon | Memorias[1].1 | Digital | Input |  | Memorias[1] B 1
8 | Temp. do Circulador Acima do Set | RA | TL | RF | Circulator | BO | TUp-Mon | RA-TL:RF-Circulator-BO:TUp-Mon | Memorias[1].2 | Digital | Input |  | Memorias[1] B 2
9 | Drift de Temp muito Alto | RA | TL | RF | Circulator | BO | TDrift-Mon | RA-TL:RF-Circulator-BO:TDrift-Mon | Memorias[1].3 | Digital | Input |  | Memorias[1] B 3
10 | Temp. Ambiente Abaixo do Set | RA | TL | RF | Circulator | BO | TEnvi-Mon | RA-TL:RF-Circulator-BO:TEnvi-Mon | Memorias[1].4 | Digital | Input |  | Memorias[1] B 4
11 | Vazão Carga 70kW | RA | TL | RF | Circulator | BO | LoadFlwRt-Mon | RA-TL:RF-Circulator-BO:LoadFlwRt-Mon | Memorias[0].31 | Digital | Input |  | Memorias[0] B 31
12 | Interlock geral Circulador | RA | TL | RF | Circulator | BO | Sts-Mon | RA-TL:RF-Circulator-BO:Sts-Mon | Memorias[5].7 | Digital | Control |  | Memorias[5] B 7
13 | Termostato Barra Dissipadora 01 | RA | ToBO | RF | HeatSink | H01 | Tms-Mon | RA-ToBO:RF-HeatSink-H01:Tms-Mon | Memorias[0].21 | Digital | Input |  | Memorias[0] B 21
14 | Termostato Barra Dissipadora 02 | RA | ToBO | RF | HeatSink | H02 | Tms-Mon | RA-ToBO:RF-HeatSink-H02:Tms-Mon | Memorias[0].22 | Digital | Input |  | Memorias[0] B 22
15 | Termostato Barra Dissipadora 03 | RA | ToBO | RF | HeatSink | H03 | Tms-Mon | RA-ToBO:RF-HeatSink-H03:Tms-Mon | Memorias[0].23 | Digital | Input |  | Memorias[0] B 23
16 | Termostato Barra Dissipadora 04 | RA | ToBO | RF | HeatSink | H04 | Tms-Mon | RA-ToBO:RF-HeatSink-H04:Tms-Mon | Memorias[0].24 | Digital | Input |  | Memorias[0] B 24
17 | Termostato Barra Dissipadora 05 | RA | ToBO | RF | HeatSink | H05 | Tms-Mon | RA-ToBO:RF-HeatSink-H05:Tms-Mon | Memorias[0].25 | Digital | Input |  | Memorias[0] B 25
18 | Termostato Barra Dissipadora 06 | RA | ToBO | RF | HeatSink | H06 | Tms-Mon | RA-ToBO:RF-HeatSink-H06:Tms-Mon | Memorias[0].26 | Digital | Input |  | Memorias[0] B 26
19 | PT - 100 Barra Dissipadora 01 | RA | ToBO | RF | HeatSink | H01 | T-Mon | RA-ToBO:RF-HeatSink-H01:T-Mon | PT_100_T_Booster_01.Ch00.Data | Analog | Input | °C | PT_100_T_Booster_01.Ch00.Data
20 | PT - 100 Barra Dissipadora 02 | RA | ToBO | RF | HeatSink | H02 | T-Mon | RA-ToBO:RF-HeatSink-H02:T-Mon | PT_100_T_Booster_01.Ch01.Data | Analog | Input | °C | PT_100_T_Booster_01.Ch01.Data
21 | PT - 100 Barra Dissipadora 03 | RA | ToBO | RF | HeatSink | H03 | T-Mon | RA-ToBO:RF-HeatSink-H03:T-Mon | PT_100_T_Booster_01.Ch02.Data | Analog | Input | °C | PT_100_T_Booster_01.Ch02.Data
22 | PT - 100 Barra Dissipadora 04 | RA | ToBO | RF | HeatSink | H04 | T-Mon | RA-ToBO:RF-HeatSink-H04:T-Mon | PT_100_T_Booster_01.Ch03.Data | Analog | Input | °C | PT_100_T_Booster_01.Ch03.Data
23 | PT - 100 Barra Dissipadora 05 | RA | ToBO | RF | HeatSink | H05 | T-Mon | RA-ToBO:RF-HeatSink-H05:T-Mon | PT_100_T_Booster_02.Ch00.Data | Analog | Input | °C | PT_100_T_Booster_02.Ch00.Data
24 | PT - 100 Barra Dissipadora 06 | RA | ToBO | RF | HeatSink | H06 | T-Mon | RA-ToBO:RF-HeatSink-H06:T-Mon | PT_100_T_Booster_02.Ch01.Data | Analog | Input | °C | PT_100_T_Booster_02.Ch01.Data
25 | Interlock Sirius | BO | 05D | RF | Intlk | - | BO-Mon | BO-05D:RF-Intlk:BO-Mon | Memorias[0].2 | Digital | Input |  | Memorias[0] B 2
26 | Sinal de erro do CLP para o LLRF | BO | 05D | RF | Intlk | - | LLRF-Mon | BO-05D:RF-Intlk:LLRF-Mon | Memorias[6].3 | Digital | Output |  | Memorias[6] B 3
27 | Emergencia sistema de interlock | BO | 05D | RF | Intlk | - | EStop-Mon | BO-05D:RF-Intlk:EStop-Mon | Memorias[1].6 | Digital | Input |  | Memorias[1] B 6
28 | Reset de Falhas - Reseta todas as falhas do sistema remotamente | BO | 05D | RF | Intlk | - | Reset-Sel | BO-05D:RF-Intlk:Reset-Sel | Memorias[5].19 | Digital | Input |  | Memorias[5] B 19
29 | LLRF Operacional | BO | 05D | RF | LLRF | - | Status-Mon | BO-05D:RF-LLRF:Status-Mon | Memorias[0].0 | Digital | Input |  | Memorias[0] B 0
30 | Interlock LLRF para o CLP | BO | 05D | RF | LLRF | - | Intlk-Mon | BO-05D:RF-LLRF:Intlk-Mon | Memorias[0].1 | Digital | Input |  | Memorias[0] B 1
31 | Termostato Pré-Amp 50 W | BO | 05D | RF | LLRFPreAmp | - | Tms-Mon | BO-05D:RF-LLRFPreAmp:Tms-Mon | N/A | Digital | Input |  | N/A
32 | PT - 100 Pré - Amplificador 50 W | BO | 05D | RF | LLRFPreAmp | - | T-Mon | BO-05D:RF-LLRFPreAmp:T-Mon | PT_100_T_Booster_02.Ch02.Data | Analog | Input | °C | PT_100_T_Booster_02.Ch02.Data
33 | Habilita Pré - Amplificador | BO | 05D | RF | LLRFPreAmp | - | Enbl-Mon | BO-05D:RF-LLRFPreAmp:Enbl-Mon | N/A | Digital | Output |  | N/A
34 | Vácuo Petra V | BO | 05D | RF | P5Cav | - | Pressure-Mon | BO-05D:RF-P5Cav:Pressure-Mon | Memorias[0].3 | Digital | Input |  | Memorias[0] B 3
35 | Petra V Termostato Disco 01 | BO | 05D | RF | P5Cav | - | Disc1Tms-Mon | BO-05D:RF-P5Cav:Disc1Tms-Mon | Memorias[0].4 | Digital | Input |  | Memorias[0] B 4
36 | Petra V Termostato Cilindro 01 | BO | 05D | RF | P5Cav | - | Cilin1Tms-Mon | BO-05D:RF-P5Cav:Cilin1Tms-Mon | Memorias[0].5 | Digital | Input |  | Memorias[0] B 5
37 | Petra V Termostato Disco 02 | BO | 05D | RF | P5Cav | - | Disc2Tms-Mon | BO-05D:RF-P5Cav:Disc2Tms-Mon | Memorias[0].6 | Digital | Input |  | Memorias[0] B 6
38 | Petra V Termostato Cilindro 02 | BO | 05D | RF | P5Cav | - | Cilin2Tms-Mon | BO-05D:RF-P5Cav:Cilin2Tms-Mon | Memorias[0].7 | Digital | Input |  | Memorias[0] B 7
39 | Petra V Termostato Disco 03 | BO | 05D | RF | P5Cav | - | Disc3Tms-Mon | BO-05D:RF-P5Cav:Disc3Tms-Mon | Memorias[0].8 | Digital | Input |  | Memorias[0] B 8
40 | Petra V Termostato Cilindro 03 | BO | 05D | RF | P5Cav | - | Cilin3Tms-Mon | BO-05D:RF-P5Cav:Cilin3Tms-Mon | Memorias[0].9 | Digital | Input |  | Memorias[0] B 9
41 | Petra V Termostato Disco 04 | BO | 05D | RF | P5Cav | - | Disc4Tms-Mon | BO-05D:RF-P5Cav:Disc4Tms-Mon | Memorias[0].10 | Digital | Input |  | Memorias[0] B 10
42 | Petra V Termostato Cilindro 04 | BO | 05D | RF | P5Cav | - | Cilin4Tms-Mon | BO-05D:RF-P5Cav:Cilin4Tms-Mon | Memorias[0].11 | Digital | Input |  | Memorias[0] B 11
43 | Petra V Termostato Disco 05 | BO | 05D | RF | P5Cav | - | Disc5Tms-Mon | BO-05D:RF-P5Cav:Disc5Tms-Mon | Memorias[0].12 | Digital | Input |  | Memorias[0] B 12
44 | Petra V Termostato Cilindro 05 | BO | 05D | RF | P5Cav | - | Cilin5Tms-Mon | BO-05D:RF-P5Cav:Cilin5Tms-Mon | Memorias[0].13 | Digital | Input |  | Memorias[0] B 13
45 | Petra V Termostato Disco 06 | BO | 05D | RF | P5Cav | - | Disc6Tms-Mon | BO-05D:RF-P5Cav:Disc6Tms-Mon | Memorias[0].14 | Digital | Input |  | Memorias[0] B 14
46 | Petra V Chave de Fluxo 01 | BO | 05D | RF | P5Cav | - | Hd1FlwRt-Mon | BO-05D:RF-P5Cav:Hd1FlwRt-Mon | Memorias[0].15 | Digital | Input |  | Memorias[0] B 15
47 | Petra V Chave de Fluxo 02 | BO | 05D | RF | P5Cav | - | Hd2FlwRt-Mon | BO-05D:RF-P5Cav:Hd2FlwRt-Mon | Memorias[0].16 | Digital | Input |  | Memorias[0] B 16
48 | Petra V Chave de Fluxo 03 | BO | 05D | RF | P5Cav | - | Hd3FlwRt-Mon | BO-05D:RF-P5Cav:Hd3FlwRt-Mon | Memorias[0].17 | Digital | Input |  | Memorias[0] B 17
49 | Petra V Sensor de Pressão | BO | 05D | RF | P5Cav | - | CoupPressure-Mon | BO-05D:RF-P5Cav:CoupPressure-Mon | Memorias[0].18 | Digital | Input |  | Memorias[0] B 18
50 | Petra V Pt - 100 Cilindro 01 | BO | 05D | RF | P5Cav | - | Cilin1T-Mon | BO-05D:RF-P5Cav:Cilin1T-Mon | PT_100_PetraV_01.Ch01.Data | Analog | Input | °C | PT_100_PetraV_01.Ch01.Data
51 | Petra V Pt - 100 Cilindro 02 | BO | 05D | RF | P5Cav | - | Cilin2T-Mon | BO-05D:RF-P5Cav:Cilin2T-Mon | PT_100_PetraV_01.Ch02.Data | Analog | Input | °C | PT_100_PetraV_01.Ch02.Data
52 | Petra V Pt - 100 Cilindro 03 | BO | 05D | RF | P5Cav | - | Cilin3T-Mon | BO-05D:RF-P5Cav:Cilin3T-Mon | PT_100_PetraV_01.Ch03.Data | Analog | Input | °C | PT_100_PetraV_01.Ch03.Data
53 | Petra V Pt - 100 Cilindro 04 | BO | 05D | RF | P5Cav | - | Cilin4T-Mon | BO-05D:RF-P5Cav:Cilin4T-Mon | PT_100_PetraV_02.Ch00.Data | Analog | Input | °C | PT_100_PetraV_02.Ch00.Data
54 | Petra V Pt - 100 Cilindro 05 | BO | 05D | RF | P5Cav | - | Cilin5T-Mon | BO-05D:RF-P5Cav:Cilin5T-Mon | PT_100_PetraV_02.Ch01.Data | Analog | Input | °C | PT_100_PetraV_02.Ch01.Data
55 | Petra V PT - 100 Acoplador | BO | 05D | RF | P5Cav | - | CoupT-Mon | BO-05D:RF-P5Cav:CoupT-Mon | PT_100_PetraV_02.Ch02.Data | Analog | Input | °C | PT_100_PetraV_02.Ch02.Data
56 | Interlock Geral Petra V | BO | 05D | RF | P5Cav | - | Sts-Mon | BO-05D:RF-P5Cav:Sts-Mon | Memorias[7].16 | Digital | Control |  | Memorias[7] B 16
57 | Potência de RF | RA | ToBO | RF | SSAmpTower | - | PwrRF-Mon | RA-ToBO:RF-SSAmpTower:PwrRF-Mon | Potencia_RF_BO | Analog | Input | dBm | Potencia_RF_BO
58 | Status do Trafo 150kVA | RA | ToBO | RF | SSAmpTower | - | PwrACOp-Mon | RA-ToBO:RF-SSAmpTower:PwrACOp-Mon | Memorias[0].19 | Digital | Input |  | Memorias[0] B 19
59 | Vazão Rotâmetro - via Skid | RA | ToBO | RF | SSAmpTower | - | HdFlwRt-Mon | RA-ToBO:RF-SSAmpTower:HdFlwRt-Mon | Memorias[0].20 | Digital | Input |  | Memorias[0] B 20
60 | Chave Pin Lenta | RA | ToBO | RF | SSAmpTower | - | PinSw-Mon | RA-ToBO:RF-SSAmpTower:PinSw-Mon | Memorias[6].1 | Digital | Output |  | Memorias[6] B 1
61 | Desliga Conversores DC/DC | RA | ToBO | RF | SSAmpTower | - | PwrCnvDsbl-Sel | RA-ToBO:RF-SSAmpTower:PwrCnvDsbl-Sel | Memorias[5].29 | Digital | Control |  | Memorias[5] B 29
62 | Liga Conversores DC/DC | RA | ToBO | RF | SSAmpTower | - | PwrCnvEnbl-Sel | RA-ToBO:RF-SSAmpTower:PwrCnvEnbl-Sel | Memorias[5].23 | Digital | Control |  | Memorias[5] B 23
63 | Leitura Conversores DC/DC | RA | ToBO | RF | SSAmpTower | - | PwrCnv-Sts | RA-ToBO:RF-SSAmpTower:PwrCnv-Sts | Memorias[6].0 | Digital | Output |  | Memorias[6] B 0
64 | Desliga 300VDC | RA | ToBO | RF | SSAmpTower | - | 300VdcDsbl-Sel | RA-ToBO:RF-SSAmpTower:300VdcDsbl-Sel | Memorias[0].27 | Digital | Control |  | Memorias[0] B 27
65 | Liga 300 VDC | RA | ToBO | RF | SSAmpTower | - | 300VdcEnbl-Sel | RA-ToBO:RF-SSAmpTower:300VdcEnbl-Sel | Memorias[0].20 | Digital | Control |  | Memorias[0] B 20
66 | Leitura Liga 300 VDC | RA | ToBO | RF | SSAmpTower | - | 300Vdc-Sts | RA-ToBO:RF-SSAmpTower:300Vdc-Sts | Memorias[6].2 | Digital | Output |  | Memorias[6] B 2
67 | Interlock Geral SSA | BO | ToBO | RF | SSAmpTower | - | Sts-Mon | BO-ToBO:RF-SSAmpTower:Sts-Mon | Memorias[5].12 | Digital | Control |  | Memorias[5] B 12
68 | Interlock geral Linha de Transmissao | RA | TL | RF | TrLine | BO | Sts-Mon | RA-TL:RF-TrLine-BO:Sts-Mon | Memorias[5].7 | Digital | Control |  | Memorias[5] B 7
69 | Entrada Analogica Reserva CLP Booster 01 | BO | 05D | RF | Intlk | In01 | AnalogSpare-Mon | BO-05D:RF-Intlk-In01:AnalogSpare-Mon | Analog_Booster_Reserva_Control_Card_04.Ch03.Data | Analog | Input |  | Analog_Booster_Reserva_Control_Card_04.Ch03.Data
70 | Entrada Analogica Reserva CLP Booster 02 | BO | 05D | RF | Intlk | In02 | AnalogSpare-Mon | BO-05D:RF-Intlk-In02:AnalogSpare-Mon | Analog_Booster_Reserva_Control_Card_05.Ch00.Data | Analog | Input |  | Analog_Booster_Reserva_Control_Card_05.Ch00.Data
71 | Entrada Analogica Reserva CLP Booster 03 | BO | 05D | RF | Intlk | In03 | AnalogSpare-Mon | BO-05D:RF-Intlk-In03:AnalogSpare-Mon | Analog_Booster_Reserva_Control_Card_05.Ch01.Data | Analog | Input |  | Analog_Booster_Reserva_Control_Card_05.Ch01.Data
72 | Entrada Analogica Reserva CLP Booster 04 | BO | 05D | RF | Intlk | In04 | AnalogSpare-Mon | BO-05D:RF-Intlk-In04:AnalogSpare-Mon | Analog_Booster_Reserva_Control_Card_05.Ch02.Data | Analog | Input |  | Analog_Booster_Reserva_Control_Card_05.Ch02.Data
73 | Entrada Analogica Reserva CLP Booster 05 | BO | 05D | RF | Intlk | In05 | AnalogSpare-Mon | BO-05D:RF-Intlk-In05:AnalogSpare-Mon | Analog_Booster_Reserva_Control_Card_05.Ch03.Data | Analog | Input |  | Analog_Booster_Reserva_Control_Card_05.Ch03.Data
74 | Entrada Analogica Reserva CLP Booster 06 | BO | 05D | RF | Intlk | In06 | AnalogSpare-Mon | BO-05D:RF-Intlk-In06:AnalogSpare-Mon | Analog_Booster_Reserva_Comapact_Card_04.Ch03.Data | Analog | Input |  | Analog_Booster_Reserva_Comapact_Card_04.Ch03.Data
75 | Entrada Analogica Reserva CLP Booster 07 | BO | 05D | RF | Intlk | In07 | AnalogSpare-Mon | BO-05D:RF-Intlk-In07:AnalogSpare-Mon | Analog_Booster_Reserva_Comapact_Card_05.Ch00.Data | Analog | Input |  | Analog_Booster_Reserva_Comapact_Card_05.Ch00.Data
76 | Entrada Analogica Reserva CLP Booster 08 | BO | 05D | RF | Intlk | In08 | AnalogSpare-Mon | BO-05D:RF-Intlk-In08:AnalogSpare-Mon | Analog_Booster_Reserva_Comapact_Card_05.Ch01.Data | Analog | Input |  | Analog_Booster_Reserva_Comapact_Card_05.Ch01.Data
77 | Entrada Analogica Reserva CLP Booster 09 | BO | 05D | RF | Intlk | In09 | AnalogSpare-Mon | BO-05D:RF-Intlk-In09:AnalogSpare-Mon | Analog_Booster_Reserva_Comapact_Card_05.Ch02.Data | Analog | Input |  | Analog_Booster_Reserva_Comapact_Card_05.Ch02.Data
78 | Entrada Analogica Reserva CLP Booster 10 | BO | 05D | RF | Intlk | In10 | AnalogSpare-Mon | BO-05D:RF-Intlk-In10:AnalogSpare-Mon | Analog_Booster_Reserva_Comapact_Card_05.Ch03.Data | Analog | Input |  | Analog_Booster_Reserva_Comapact_Card_05.Ch03.Data
79 | Entrada Analogica Reserva CLP Booster 11 | BO | 05D | RF | Intlk | In11 | AnalogSpare-Mon | BO-05D:RF-Intlk-In11:AnalogSpare-Mon | Analog_Booster_Reserva_Comapact_Card_06.Ch00.Data | Analog | Input |  | Analog_Booster_Reserva_Comapact_Card_06.Ch00.Data
80 | Entrada Analogica Reserva CLP Booster 12 | BO | 05D | RF | Intlk | In12 | AnalogSpare-Mon | BO-05D:RF-Intlk-In12:AnalogSpare-Mon | Analog_Booster_Reserva_Comapact_Card_06.Ch01.Data | Analog | Input |  | Analog_Booster_Reserva_Comapact_Card_06.Ch01.Data
81 | Entrada Analogica Reserva CLP Booster 13 | BO | 05D | RF | Intlk | In13 | AnalogSpare-Mon | BO-05D:RF-Intlk-In13:AnalogSpare-Mon | Analog_Booster_Reserva_Comapact_Card_06.Ch02.Data | Analog | Input |  | Analog_Booster_Reserva_Comapact_Card_06.Ch02.Data
82 | Entrada Analogica Reserva CLP Booster 14 | BO | 05D | RF | Intlk | In14 | AnalogSpare-Mon | BO-05D:RF-Intlk-In14:AnalogSpare-Mon | Analog_Booster_Reserva_Comapact_Card_06.Ch03.Data | Analog | Input |  | Analog_Booster_Reserva_Comapact_Card_06.Ch03.Data
83 | Entrada Analogica Reserva CLP Booster 15 | BO | 05D | RF | Intlk | In15 | AnalogSpare-Mon | BO-05D:RF-Intlk-In15:AnalogSpare-Mon | Analog_Booster_Reserva_Comapact_Card_07.Ch00.Data | Analog | Input |  | Analog_Booster_Reserva_Comapact_Card_07.Ch00.Data
84 | Entrada Analogica Reserva CLP Booster 16 | BO | 05D | RF | Intlk | In16 | AnalogSpare-Mon | BO-05D:RF-Intlk-In16:AnalogSpare-Mon | Analog_Booster_Reserva_Comapact_Card_07.Ch01.Data | Analog | Input |  | Analog_Booster_Reserva_Comapact_Card_07.Ch01.Data
85 | Entrada Analogica Reserva CLP Booster 17 | BO | 05D | RF | Intlk | In17 | AnalogSpare-Mon | BO-05D:RF-Intlk-In17:AnalogSpare-Mon | Analog_Booster_Reserva_Comapact_Card_07.Ch02.Data | Analog | Input |  | Analog_Booster_Reserva_Comapact_Card_07.Ch02.Data
86 | Entrada Analogica Reserva CLP Booster 18 | BO | 05D | RF | Intlk | In18 | AnalogSpare-Mon | BO-05D:RF-Intlk-In18:AnalogSpare-Mon | Analog_Booster_Reserva_Comapact_Card_07.Ch03.Data | Analog | Input |  | Analog_Booster_Reserva_Comapact_Card_07.Ch03.Data
87 | Entrada Digital Reserva CLP Booster 01 | BO | 05D | RF | Intlk | In01 | DigitalSpare-Mon | BO-05D:RF-Intlk-In01:DigitalSpare-Mon | IN_Dig_Booster_Reserva_Control_Card_02.Pt14.Data | Digital | Input |  | IN_Dig_Booster_Reserva_Control_Card_02.Pt14.Data
88 | Entrada Digital Reserva CLP Booster 02 | BO | 05D | RF | Intlk | In02 | DigitalSpare-Mon | BO-05D:RF-Intlk-In02:DigitalSpare-Mon | IN_Dig_Booster_Reserva_Control_Card_02.Pt15.Data | Digital | Input |  | IN_Dig_Booster_Reserva_Control_Card_02.Pt15.Data
89 | Entrada Digital Reserva CLP Booster 03 | BO | 05D | RF | Intlk | In03 | DigitalSpare-Mon | BO-05D:RF-Intlk-In03:DigitalSpare-Mon | IN_Dig_Booster_Reserva_Compact_Card_01.Pt09.Data | Digital | Input |  | IN_Dig_Booster_Reserva_Compact_Card_01.Pt09.Data
90 | Entrada Digital Reserva CLP Booster 04 | BO | 05D | RF | Intlk | In04 | DigitalSpare-Mon | BO-05D:RF-Intlk-In04:DigitalSpare-Mon | IN_Dig_Booster_Reserva_Compact_Card_01.Pt10.Data | Digital | Input |  | IN_Dig_Booster_Reserva_Compact_Card_01.Pt10.Data
91 | Entrada Digital Reserva CLP Booster 05 | BO | 05D | RF | Intlk | In05 | DigitalSpare-Mon | BO-05D:RF-Intlk-In05:DigitalSpare-Mon | IN_Dig_Booster_Reserva_Compact_Card_01.Pt11.Data | Digital | Input |  | IN_Dig_Booster_Reserva_Compact_Card_01.Pt11.Data
92 | Entrada Digital Reserva CLP Booster 06 | BO | 05D | RF | Intlk | In06 | DigitalSpare-Mon | BO-05D:RF-Intlk-In06:DigitalSpare-Mon | IN_Dig_Booster_Reserva_Compact_Card_01.Pt12.Data | Digital | Input |  | IN_Dig_Booster_Reserva_Compact_Card_01.Pt12.Data
93 | Entrada Digital Reserva CLP Booster 07 | BO | 05D | RF | Intlk | In07 | DigitalSpare-Mon | BO-05D:RF-Intlk-In07:DigitalSpare-Mon | IN_Dig_Booster_Reserva_Compact_Card_01.Pt13.Data | Digital | Input |  | IN_Dig_Booster_Reserva_Compact_Card_01.Pt13.Data
94 | Entrada Digital Reserva CLP Booster 08 | BO | 05D | RF | Intlk | In08 | DigitalSpare-Mon | BO-05D:RF-Intlk-In08:DigitalSpare-Mon | IN_Dig_Booster_Reserva_Compact_Card_01.Pt14.Data | Digital | Input |  | IN_Dig_Booster_Reserva_Compact_Card_01.Pt14.Data
95 | Entrada Digital Reserva CLP Booster 09 | BO | 05D | RF | Intlk | In09 | DigitalSpare-Mon | BO-05D:RF-Intlk-In09:DigitalSpare-Mon | IN_Dig_Booster_Reserva_Compact_Card_01.Pt15.Data | Digital | Input |  | IN_Dig_Booster_Reserva_Compact_Card_01.Pt15.Data
96 | Entrada Digital Reserva CLP Booster 10 | BO | 05D | RF | Intlk | In10 | DigitalSpare-Mon | BO-05D:RF-Intlk-In10:DigitalSpare-Mon | IN_Dig_Booster_Reserva_Compact_Card_02.Pt00.Data | Digital | Input |  | IN_Dig_Booster_Reserva_Compact_Card_02.Pt00.Data
97 | Entrada Digital Reserva CLP Booster 11 | BO | 05D | RF | Intlk | In11 | DigitalSpare-Mon | BO-05D:RF-Intlk-In11:DigitalSpare-Mon | IN_Dig_Booster_Reserva_Compact_Card_02.Pt01.Data | Digital | Input |  | IN_Dig_Booster_Reserva_Compact_Card_02.Pt01.Data
98 | Entrada Digital Reserva CLP Booster 12 | BO | 05D | RF | Intlk | In12 | DigitalSpare-Mon | BO-05D:RF-Intlk-In12:DigitalSpare-Mon | IN_Dig_Booster_Reserva_Compact_Card_02.Pt02.Data | Digital | Input |  | IN_Dig_Booster_Reserva_Compact_Card_02.Pt02.Data
99 | Entrada Digital Reserva CLP Booster 13 | BO | 05D | RF | Intlk | In13 | DigitalSpare-Mon | BO-05D:RF-Intlk-In13:DigitalSpare-Mon | IN_Dig_Booster_Reserva_Compact_Card_02.Pt03.Data | Digital | Input |  | IN_Dig_Booster_Reserva_Compact_Card_02.Pt03.Data
100 | Entrada Digital Reserva CLP Booster 14 | BO | 05D | RF | Intlk | In14 | DigitalSpare-Mon | BO-05D:RF-Intlk-In14:DigitalSpare-Mon | IN_Dig_Booster_Reserva_Compact_Card_02.Pt04.Data | Digital | Input |  | IN_Dig_Booster_Reserva_Compact_Card_02.Pt04.Data
101 | Entrada Digital Reserva CLP Booster 15 | BO | 05D | RF | Intlk | In15 | DigitalSpare-Mon | BO-05D:RF-Intlk-In15:DigitalSpare-Mon | IN_Dig_Booster_Reserva_Compact_Card_02.Pt05.Data | Digital | Input |  | IN_Dig_Booster_Reserva_Compact_Card_02.Pt05.Data
102 | Entrada Digital Reserva CLP Booster 16 | BO | 05D | RF | Intlk | In16 | DigitalSpare-Mon | BO-05D:RF-Intlk-In16:DigitalSpare-Mon | IN_Dig_Booster_Reserva_Compact_Card_02.Pt06.Data | Digital | Input |  | IN_Dig_Booster_Reserva_Compact_Card_02.Pt06.Data
103 | Entrada Digital Reserva CLP Booster 17 | BO | 05D | RF | Intlk | In17 | DigitalSpare-Mon | BO-05D:RF-Intlk-In17:DigitalSpare-Mon | IN_Dig_Booster_Reserva_Compact_Card_02.Pt07.Data | Digital | Input |  | IN_Dig_Booster_Reserva_Compact_Card_02.Pt07.Data
104 | Entrada Digital Reserva CLP Booster 18 | BO | 05D | RF | Intlk | In18 | DigitalSpare-Mon | BO-05D:RF-Intlk-In18:DigitalSpare-Mon | IN_Dig_Booster_Reserva_Compact_Card_02.Pt08.Data | Digital | Input |  | IN_Dig_Booster_Reserva_Compact_Card_02.Pt08.Data
105 | Entrada Digital Reserva CLP Booster 19 | BO | 05D | RF | Intlk | In19 | DigitalSpare-Mon | BO-05D:RF-Intlk-In19:DigitalSpare-Mon | IN_Dig_Booster_Reserva_Compact_Card_02.Pt09.Data | Digital | Input |  | IN_Dig_Booster_Reserva_Compact_Card_02.Pt09.Data
106 | Entrada Digital Reserva CLP Booster 20 | BO | 05D | RF | Intlk | In20 | DigitalSpare-Mon | BO-05D:RF-Intlk-In20:DigitalSpare-Mon | IN_Dig_Booster_Reserva_Compact_Card_02.Pt10.Data | Digital | Input |  | IN_Dig_Booster_Reserva_Compact_Card_02.Pt10.Data
107 | Entrada Digital Reserva CLP Booster 21 | BO | 05D | RF | Intlk | In21 | DigitalSpare-Mon | BO-05D:RF-Intlk-In21:DigitalSpare-Mon | IN_Dig_Booster_Reserva_Compact_Card_02.Pt11.Data | Digital | Input |  | IN_Dig_Booster_Reserva_Compact_Card_02.Pt11.Data
108 | Entrada Digital Reserva CLP Booster 22 | BO | 05D | RF | Intlk | In22 | DigitalSpare-Mon | BO-05D:RF-Intlk-In22:DigitalSpare-Mon | IN_Dig_Booster_Reserva_Compact_Card_02.Pt12.Data | Digital | Input |  | IN_Dig_Booster_Reserva_Compact_Card_02.Pt12.Data
109 | Entrada Digital Reserva CLP Booster 23 | BO | 05D | RF | Intlk | In23 | DigitalSpare-Mon | BO-05D:RF-Intlk-In23:DigitalSpare-Mon | IN_Dig_Booster_Reserva_Compact_Card_02.Pt13.Data | Digital | Input |  | IN_Dig_Booster_Reserva_Compact_Card_02.Pt13.Data
110 | Entrada Digital Reserva CLP Booster 24 | BO | 05D | RF | Intlk | In24 | DigitalSpare-Mon | BO-05D:RF-Intlk-In24:DigitalSpare-Mon | IN_Dig_Booster_Reserva_Compact_Card_02.Pt14.Data | Digital | Input |  | IN_Dig_Booster_Reserva_Compact_Card_02.Pt14.Data
111 | Entrada Digital Reserva CLP Booster 25 | BO | 05D | RF | Intlk | In25 | DigitalSpare-Mon | BO-05D:RF-Intlk-In25:DigitalSpare-Mon | IN_Dig_Booster_Reserva_Compact_Card_02.Pt15.Data | Digital | Input |  | IN_Dig_Booster_Reserva_Compact_Card_02.Pt15.Data
112 | Saída Digital Reserva CLP Booster 01 | BO | 05D | RF | Intlk | Out01 | DigitalSpare-Mon | BO-05D:RF-Intlk-Out01:DigitalSpare-Mon | Out_Dig_Booster_Reserva_Control_Card_06.Pt03.Data | Digital | Output |  | Out_Dig_Booster_Reserva_Control_Card_06.Pt03.Data
113 | Saída Digital Reserva CLP Booster 02 | BO | 05D | RF | Intlk | Out02 | DigitalSpare-Mon | BO-05D:RF-Intlk-Out02:DigitalSpare-Mon | Out_Dig_Booster_Reserva_Control_Card_06.Pt04.Data | Digital | Output |  | Out_Dig_Booster_Reserva_Control_Card_06.Pt04.Data
114 | Saída Digital Reserva CLP Booster 03 | BO | 05D | RF | Intlk | Out03 | DigitalSpare-Mon | BO-05D:RF-Intlk-Out03:DigitalSpare-Mon | Out_Dig_Booster_Reserva_Control_Card_06.Pt05.Data | Digital | Output |  | Out_Dig_Booster_Reserva_Control_Card_06.Pt05.Data
115 | Saída Digital Reserva CLP Booster 04 | BO | 05D | RF | Intlk | Out04 | DigitalSpare-Mon | BO-05D:RF-Intlk-Out04:DigitalSpare-Mon | Out_Dig_Booster_Reserva_Control_Card_06.Pt06.Data | Digital | Output |  | Out_Dig_Booster_Reserva_Control_Card_06.Pt06.Data
116 | Saída Digital Reserva CLP Booster 05 | BO | 05D | RF | Intlk | Out05 | DigitalSpare-Mon | BO-05D:RF-Intlk-Out05:DigitalSpare-Mon | Out_Dig_Booster_Reserva_Control_Card_06.Pt07.Data | Digital | Output |  | Out_Dig_Booster_Reserva_Control_Card_06.Pt07.Data
117 | Saída Digital Reserva CLP Booster 06 | BO | 05D | RF | Intlk | Out06 | DigitalSpare-Mon | BO-05D:RF-Intlk-Out06:DigitalSpare-Mon | Out_Dig_Booster_Reserva_Control_Card_06.Pt08.Data | Digital | Output |  | Out_Dig_Booster_Reserva_Control_Card_06.Pt08.Data
118 | Saída Digital Reserva CLP Booster 07 | BO | 05D | RF | Intlk | Out07 | DigitalSpare-Mon | BO-05D:RF-Intlk-Out07:DigitalSpare-Mon | Out_Dig_Booster_Reserva_Control_Card_06.Pt09.Data | Digital | Output |  | Out_Dig_Booster_Reserva_Control_Card_06.Pt09.Data
119 | Saída Digital Reserva CLP Booster 08 | BO | 05D | RF | Intlk | Out08 | DigitalSpare-Mon | BO-05D:RF-Intlk-Out08:DigitalSpare-Mon | Out_Dig_Booster_Reserva_Compact_Card_08.Pt04.Data | Digital | Output |  | Out_Dig_Booster_Reserva_Compact_Card_08.Pt04.Data
120 | Saída Digital Reserva CLP Booster 09 | BO | 05D | RF | Intlk | Out09 | DigitalSpare-Mon | BO-05D:RF-Intlk-Out09:DigitalSpare-Mon | Out_Dig_Booster_Reserva_Compact_Card_08.Pt05.Data | Digital | Output |  | Out_Dig_Booster_Reserva_Compact_Card_08.Pt05.Data
121 | Saída Digital Reserva CLP Booster 10 | BO | 05D | RF | Intlk | Out10 | DigitalSpare-Mon | BO-05D:RF-Intlk-Out10:DigitalSpare-Mon | Out_Dig_Booster_Reserva_Compact_Card_08.Pt06.Data | Digital | Output |  | Out_Dig_Booster_Reserva_Compact_Card_08.Pt06.Data
122 | Saída Digital Reserva CLP Booster 11 | BO | 05D | RF | Intlk | Out11 | DigitalSpare-Mon | BO-05D:RF-Intlk-Out11:DigitalSpare-Mon | Out_Dig_Booster_Reserva_Compact_Card_08.Pt07.Data | Digital | Output |  | Out_Dig_Booster_Reserva_Compact_Card_08.Pt07.Data
Note on B12: Variaveis relativas a carga de RF podem ser alocadas junto ao circulador, dado que ela esta acoplada diretamente com o circulador.
Note on B13: Necessário explicação da aplicação.
Note on A14: Ranieri Ramires do Canto Santos: Da Variável 13 a 16 ainda não esta definido.